## BOQ SUMMARY PAGE
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Total
SUMMARY OF BILL OF QUANTITIES
1 | Building Works | 0
2 | Server Room | 0
3 | Electrical allowwance for COC | 0
4 | HVAC | 0
5 | General | 0
6 | 5yr Maintenance | 0
| Total Value Including VAT | 0

## 1. BUILDING WORKS
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Qty | Rate | Total incl. VAT
1. BUILDING WORKS
1 | SERVER ROOM
1.1 | Close off working area for new server room before construction and remove after construction | 1 | 0 | 0
1.2 | Remove existing ceiling for server room space | 1 | 0 | 0
1.3 | Level existing slab in server room space | 1 | 0 | 0
1.4 | Rubble removal | 1 | 0 | 0
1.5 | Supply & install 2hr Fire Rated drywall - double skin - 3400mm (H) slab to slab to construct new server room. 2 walls in addition to the 2 x existing brick walls | 1 | 0 | 0
1.6 | Close up existing glass openings in existing brick wall | 1 | 0 | 0
1.7 | Supply & install steel corner beads to corners | 1 | 0 | 0
1.8 | Supply & install aluminium skirting | 1 | 0 | 0
1.9 | Supply 2hr Fire Rated double door & frame - 1600 x 2032 | 1 | 0 | 0
1.1 | Supply & install push/pull handles | 1 | 0 | 0
1.11 | Supply & install 3 lever high security lockset | 1 | 0 | 0
1.12 | Supply & install heavy duty door closer EN1154 fire rated | 1 | 0 | 0
1.13 | Supply & install std door stoppers | 1 | 0 | 0
1.14 | Supply plaster primer & 2 coats fire rated Velvet Sheen to new drywall - Std Colours | 1 | 0 | 0
1.15 | Patch existing wall, apply primer & 2 coats fire rated Velvet Sheen - to walls affected by drywalls | 1 | 0 | 0
1.16 | Prep & paint std doors with enamel - std colours | 1 | 0 | 0
1.17 | Provision to touch up fire rated paint after construction | 1 | 0 | 0
1.18 | Supply & fit suspended ceilings as required - 600 x 600 white vinyl tiles | 1 | 0 | 0
1.19 | Supply & install shadow line trim 20x20 to exterior walls | 1 | 0 | 0
1.2 | Deep impact clean using specialised data centre cleaning crews | 2 | 0 | 0
2 | UPS ROOMS
2.1 | Uplift and remove paving for UPS rooms space | 1 | 0 | 0
2.2 | Prepare area once paving removed to construct UPS rooms | 1 | 0 | 0
2.3 | Supply and install double brick wall to construct UPS rooms A and B with a raised door opening | 1 | 0 | 0
2.4 | Exterior water proofing around new UPS rooms 200mm from ground based on building standards around exposed perimeter walls of UPS room | 1 | 0 | 0
2.5 | Brick up opening in existing side wall | 1 | 0 | 0
2.6 | Prepare existing slab above and pillars to receive new paint | 1 | 0 | 0
2.7 | Supply and install 2hr fire rated 1½ leaf exterior doors | 1 | 0 | 0
2.8 | Supply & install push/pull handles | 1 | 0 | 0
2.9 | Supply & install 3 lever high security lockset | 1 | 0 | 0
2.10 | Supply & install heavy duty door closer EN1154 fire rated | 1 | 0 | 0
2.11 | Supply & install std door stoppers | 1 | 0 | 0
2.12 | Plaster and paint all interior and exterior walls for new UPS rooms | 1 | 0 | 0
2.13 | Paint existing slab above and pillars | 1 | 0 | 0
2.14 | Re-instate and level paving around new UPS rooms | 1 | 0 | 0
2.15 | Supply and install canopies over new doors | 1 | 0 | 0
2.16 | Paint new doors | 1 | 0 | 0
2.17 | Rubble removal | 1 | 0 | 0
2.18 | Provision to touch up paint after construction | 1 | 0 | 0
2.19 | Deep impact clean using specialised data centre cleaning crews | 2 | 0 | 0
3 | LOW VOLTAGE ROOM (BASEMENT)
3.1 | Level existing slab in LV room space | 1 | 0 | 0
3.2 | Remove exiting door and frame | 1 | 0 | 0
3.3 | Exterior water proofing around new LV room 200mm from ground | 1 | 0 | 0
3.4 | Prepare existing slab above to receive new paint | 1 | 0 | 0
3.5 | Supply 2hr Fire Rated double door & frame including push/pull handles, 3 lever lockset, heavy duty door closer EN1154 fire rated and std door stoppers | 1 | 0 | 0
3.6 | Plaster and paint all interior and exterior walls for new LV room | 1 | 0 | 0
3.7 | Paint existing slab above | 1 | 0 | 0
3.8 | Paint slab below | 1 | 0 | 0
3.9 | Paint new doors | 1 | 0 | 0
3.1 | Rubble removal | 1 | 0 | 0
3.11 | Remove sprinkler pipe | 1 | 0 | 0
3.12 | Raise door opening from ground level | 1 | 0 | 0
3.13 | Waterproof around the exterior of LV room |  | 0
3.14 | Deep impact clean using specialised data centre cleaning crews | 1 | 0 | 0
3.15 | Provision to touch up paint after construction | 1 | 0 | 0
4 | GENERATOR AREA
4.1 | Supply and install concrete slab for new generator | 1 | 0 | 0
4.2 | Supply and install palisade fence and gate to match existing around new generator | 1 | 0 | 0
5 | GENERAL
5.1 | Sundries @ max 5% of Bill 1 value | 1 | 0 | 0
5.2 | Labour | 1 | 0 | 0
5.3 | Any additional equipment necessary to complete the installation, but not allowed elsewhere in the bill of quantities. | 1 | 0 | 0
| Total Including Vat |  |  | 0

## 2. SERVER ROOM
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Qty | Rate | Total incl. VAT
2. SERVER ROOM
1 | ACCESS FLOORING (SERVER ROOM)
1.1 | m2 600mm raised access floor (1200kg/m2 UDL) | 60 | 0 | 0
1.2 | Sealing and marking slab below | 1 | 0 | 0
1.3 | Perimeter cutting | 1 | 0 | 0
1.4 | Double cup lifters | 2 | 0 | 0
1.5 | Cut outs | 10 | 0 | 0
1.6 | Rack cut outs with brush panels | 10 | 0 | 0
1.7 | Double door well and step | 1 | 0 | 0
1.8 | Skirting | 1 | 0 | 0
2 | ACCESS FLOORING (UPS ROOMS 1 & 2)
2.1 | m2 200mm raised access floor (1200kg/m2 UDL) | 40 | 0 | 0
2.2 | Sealing and marking slab below | 1 | 0 | 0
2.3 | Perimeter cutting | 1 | 0 | 0
2.4 | Double cup lifters | 2 | 0 | 0
2.5 | Cut outs | 10 | 0 | 0
2.6 | UPS floor stands | 2 | 0 | 0
2.7 | Battery cabinet floor stands | 2 | 0 | 0
2.8 | Aluminium Skirting as specified | 1 | 0 | 0
3 | FIRE SUPPRESSION AND DETECTION
3.1 | 210m³ room size: Server Room Complete NOVEC 1230 fire suppression and detection system for the server room to detect in and protect all 3 voids including and not limited to panels, sounders, beacons, zonal diagram, call points, lockable enclosure for fire panel, cylinder straps, bosal pipe routing, fire cables, detectors, monitoring output relays x 4 and integrity test | 1 | 0 | 0
3.2 | 68m³ room size: UPS Room A Complete NOVEC 1230 fire suppression and detection system for UPS Room A to detect and protect room void including and not limited to panels, sounders, beacons, zonal diagram, call points, IP rated outdoor lockable enclosure for fire panel, cylinder straps, bosal pipe routing, fire cables, detectors, monitoring output relays x 4, 1 x hydrogen sensor and integrity test | 1 | 0 | 0
3.3 | 68m³ room size: UPS Room B Complete NOVEC 1230 fire suppression and detection system for UPS Room B to detect and protect room void including and not limited to panels, sounders, beacons, zonal diagram, call points, IP rated outdoor lockable enclosure for fire panel, cylinder straps, bosal pipe routing, fire cables, detectors, monitoring output relays x 4, 1 x hydrogen sensor and integrity test | 1 | 0 | 0
3.4 | 80m³ room size: LV Room Complete NOVEC 1230 fire suppression and detection system for UPS Room B to detect and protect room void including and not limited to panels, sounders, beacons, zonal diagram, call points, IP rated outdoor lockable enclosure for fire panel, cylinder straps, bosal pipe routing, fire cables, detectors, monitoring output relays x 4, 1 x hydrogen sensor and integrity test | 1 | 0 | 0
3.5 | Early detection system per room | 4 | 0 | 0
3.6 | Wall mount fire extinguishers for each room ( 2 x 4,5 kg CO2) complete with wall bracket & signage | 8 | 0 | 0
3.7 | Repeater panel installed at reception/security with all 4 x zones monitoring capabilities, complete with alarm, zonal diagram, complete | 1 | 0 | 0
4 | ENVIRONMENTAL MONITORING (TM4)
4.1 | Complete TM4 monitoring system solution for the server room including GSM modem, temperature and humidity sensors for each rack, door contact, perimeter flood strip and flood strip per row under floor, dry contacts for all equipment, 48 port dry contact module, 4 x dry contacts for each generator, fire system, Fresh air system, ATS units, Cooling units, UPS in general DB, enclosure, installation, configuration and training. Cable to be yellow Cat6 Krone where required | 1 | 0 | 0
4.2 | Environmental monitoring system similar or equivalent to TM4 monitoring system solution for UPS room A including GSM modem, temperature sensors for the room, door contact, perimeter and equipment flood strip, dry contacts for UPS, cooling units, ATS units, fire system, 48 port dry contact module, enclosure, installation, configuration and training. Cable to be yellow Cat6 Krone where required | 1 | 0 | 0
4.3 | Environmental monitoring system similar or equivalent to TM4 monitoring system solution for UPS room B including GSM modem, temperature sensors for the room, door contact, perimeter and equipment flood strip, dry contacts for UPS, cooling units, ATS units, fire system, 48 port dry contact module, enclosure, installation, configuration and training. Cable to be yellow Cat6 Krone where required | 1 | 0 | 0
4.4 | Environmental monitoring system similar or equivalent to TM4 monitoring system solution for LV room including GSM modem, temperature sensors for the room, door contact, perimeter and equipment flood strip, dry contacts for UPS, cooling units, ATS units, fire system, 48 port dry contact module, enclosure, installation, configuration and training. Cable to be yellow Cat6 Krone where required | 1 | 0 | 0
5 | INTEGRATED SECURITY
5.1 | Complete access system with biometric reader in, no touch push button exit, heavy duty mag locks, fire rated door closers, power supplies, controllers, PC, software, enrolment reader and installation for 4 rooms | 1 | 0 | 0
6 | RACKS AND PDU's (RITTAL, VERTIV, DELTA)
6.1 | 42U, 800mm x 1200mm front and rear vented racks, split rear doors, side panels, brush cable entries top and bottom. | 6 | 0 | 0
6.2 | Brush air baffle panels to be installed in each rack on either side between profile posts and side panels | 6 | 0 | 0
6.3 | Vertical Cable Management 150-200mm wide | 12 | 0 | 0
6.4 | Levelling Feet | 6 | 0 | 0
6.5 | Gland Plates Complete | 6 | 0 | 0
6.6 | Horizontal ring cable manager | 24 | 0 | 0
6.7 | Blanking panels 1U | 180 | 0 | 0
6.8 | 32A 1phase vertical 0U PDU, Metered with 20 x C13 and 4 x C19 ports including cable and IEC connector | 12 | 0 | 0
6 | GENERAL
5.1 | Sundries @ max 5% of Bill 2 value | 1 | 0 | 0
5.2 | Labour | 1 | 0 | 0
5.3 | Commissioning of Server room, Cooling tests, Fire Tests, Load tests, monitoring tests and mains fail tests. | 1 | 0 | 0
5.4 | Any additional equipment necessary to complete the installation, but not allowed elsewhere in the bill of quantities. | 1 | 0 | 0
| Total Including Vat |  |  | 0

## 3. ELECTRICAL
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Qty | Rate | Total incl. VAT
3. ELECTRICAL
1 | GENERATOR
1.1 | 400kVA Prime Generator complete with Automatic Change, Tier 3 emission rated, 372 kW (1500 rpm), 1000 litre base diesel tank, heater, residential muffler, oil pressure, engine temp, and fuel to read off Deep SEA 8610 Auto start controller.as specified, 20% Dummy load. | 1 | 0 | 0
1.2 | Engine-Co custom sound and weather proof mild steel canopy (Noise not to exceed 65DB at 1m) | 1 | 0 | 0 | 721.709
1.3 | Engine-Co custom generator sync changeover panel 1000A to accommodate sync between 2 x 400kVA generators (1 @day 1 and 1 in the future), automatic trayfer between 1000A Utility feed and the 2 x generator feeds, 1 x 800A output for the building, 1 x 250A output for Server Room and 1 x 160A output for building UPS | 1 | 0 | 0
1.4 | Delivery and commissioning | 1 | 0 | 0
1.5 | 1000L diesel | 1 | 0 | 0
1.6 | Major service of the existing 200kVA generator | 1 | 0 | 0
1.7 | New batteries for existing 200kVA generator | 2 | 0 | 0
1.8 | Provisional SUM for Structural engineer to confirm and provide approval to place the new 400kVA generator next to the existing generator | 1 | 0 | 0
2 | UPS Similar or Equaivalkent to (DELTA, VERTIV, RIELLO, EATON)
Server Room
2.1 | 60kVA UPS | 2 | 0 | 0
2.2 | Battery cabinet including batteries with links, DC cables, DC fuse/circuit breaker and to provide 15min @ 40kW load | 2 | 0 | 0
2.3 | Battery set up | 2 | 0 | 0
2.4 | Commissioning | 2 | 0 | 0
2.5 | SNMP card | 2 | 0 | 0
2.6 | Delivery | 2 | 0 | 0
Building
2.7 | Modular UPS - At day 1 to be installed with minimum 50kW power modules for N capacity plus an additional module for redundancy. Modular UPS chassis must be sufficient in size to be populated in the future with minimum 100kW of power modules for N capacity plus and additional module for redundancy | 1 | 0 | 0
2.8 | Battery cabinet including batteries with links, DC cables, DC fuse/circuit breaker and to provide 15min @ 50kW load | 1 | 0 | 0
2.9 | Commissioning | 1 | 0 | 0
2.1 | Battery set up | 1 | 0 | 0
2.11 | Simple Network Management Protocol (SNMP) card | 1 | 0 | 0
2.12 | Delivery | 1 | 0 | 0
3 | ELECTRICAL RETICULATION - Splitter Panel
3.1 | MV switching after hours | 1 | 0 | 0
3.2 | New LV splitter panel | 1 | 0 | 0
3.3 | Supply and install new PVC/PVC/SWA/PVC low halogen 600/1000V copper cables comlpete with kwena earth cable equivalent to half of copper cable on phase cable from LV side of trayformer to new splitter panel input including all materials and terminations. | 1 | 0 | 0
3.4 | Supply and install new PVC/PVC/SWA/PVC low halogen 600/1000V copper cables comlpete with kwena earth cable equivalent to half of copper cable on phase cable from new splitter panel output to new generator sync changeover panel including all materials | 1 | 0 | 0
3.5 | Supply and install new PVC/PVC/SWA/PVC low halogen 600/1000V copper cables comlpete with kwena earth cable equivalent to half of copper cable on phase cable from new generator sync changeover panel to existing building LV panel including all materials | 1 | 0 | 0
3.6 | Supply and install all routing required for all the above cables. Cables to be on cable trays and or cable ladders able to carry the weight of the cable the cable trays to be supported as per the manufacturer's recommendation. | 1 | 0 | 0
3.7 | Portable generator with sufficient lighting and power for working during shut down | 1 | 0 | 0
4 | ELECTRICAL RETICULATION - 400kVA Generator
4.1 | Supply and install new PVC/PVC/SWA/PVC low halogen 600/1000V copper cables comlpete with kwena earth cable equivalent to half of copper cable on phase cable from from new 400kVA generator to new generator sync changeover panel including terminations and all material other material for complete and compliant installations | 1 | 0 | 0
4.2 | Core drills for all cable routes to basement | 1 | 0 | 0
4.3 | Supply and install all routing required for all the above cables. Cables to be on cable trays and or cable ladders able to carry the weight of the cable the cable trays to be supported as per the manufacturer's recommendation. | 1 | 0 | 0
5 | ELECTRICAL RETICULATION - Existing Generator and Server Room A Feed
5.1 | Supply and install new LV cables and earth from new splitter panel to existing generator including all materials | 1 | 0 | 0
5.1 | Supply and install new LV cables and earth from existing generator to Server Room Generator DB A including all materials | 1 | 0 | 0
5.1 | Core drills for all cable routes to basement | 1 | 0 | 0
5.1 | Supply and install all routing required | 1 | 0 | 0
6 | ELECTRICAL RETICULATION - Server Room B Feed
6.1 | cable on phase cable from new generator sync changeover panel to Server Room Generator DB B including all materials | 1 | 0 | 0
6.2 | Core drills for all cable routes to basement | 1 | 0 | 0
6.3 | Supply and install all routing required for all the above cables. Cables to be on cable trays and or cable ladders able to carry the weight of the cable the cable trays to be supported as per the manufacturer's recommendation. | 1 | 0 | 0
7 | ELECTRICAL RETICULATION - Server Room
7.1 | Generator DB's complete with main input C/B, UPS input and Bypass circuit breakers, wrap around C/B, cooling units indoor and outdoor C/B's, Split cooling units C/B's, DC fresh air fan system C/B, future C/B's for cooling units, spares and Surge protection | 2 | 0 | 0
7.2 | UPS DB's complete with main input C/B, wrap around C/B, feeds to the racks, feed to the general DB, feeds to lighting circuits in all rooms, spare C/B's and Surge protection | 2 | 0 | 0
7.3 | General DB complete with built in ATS and UPS including A and B UPS fed inputs for all auxiliary equipment such as the fire systems, early warning systems, monitoring systems and lighting in all rooms | 1 | 0 | 0
7.4 | UPS rectifier and bypass inputs including SWA electrical cable, ICEW cable, routing, lugs, glands, shrouds and terminations. Fed from Gen DB A and B to each UPS | 2 | 0 | 0
7.5 | UPS outputs to UPS DB's including SWA electrical cable, ICEW cable, routing, lugs, glands, shrouds and terminations. | 2 | 0 | 0
7.6 | UPS wrap around | 2 | 0 | 0
7.7 | General white plug circuits | 5 | 0 | 0
7.8 | Generator A feeds for the cooling units in the DC including isolators, cables and terminations | 2 | 0 | 0
7.9 | Generator B feeds for the cooling units in the DC including isolators, cables and terminations | 2 | 0 | 0
7.1 | Generator A feeds for the cooling units in the UPS Rooms including isolators, cables and terminations | 4 | 0 | 0
7.11 | Generator B feeds for the cooling units in the UPS Rooms including isolators, cables and terminations | 4 | 0 | 0
7.12 | Generator A feeds for the fresh air system in the DC including isolators, cables and terminations | 1 | 0 | 0
7.13 | Generator B feeds for the fresh air system in the DC including isolators, cables and terminations | 1 | 0 | 0
7.14 | Feeds to the fire systems (A and B) for each room | 3 | 0 | 0
7.15 | 32A UPS feeds to each rack A and B | 16 | 0 | 0
7.16 | Lighting circuits server room and both UPS rooms with switches split between the 2 x UPS DB's an general DB | 1 | 0 | 0
7.17 | LED light fittings complete motion sensor switch and manual switch at the door for server room and both UPS rooms | 1 | 0 | 0
7.18 | Emergency battery backed up LED light fittings complete for server room and both UPS rooms | 1 | 0 | 0
7.19 | 2 x earth bars under floor in the server room including 16mm cable to each rack and every second floor pedestal, 2 x 70mm earth cables to each earth bar fed from main building earth, 2 x 70mm cables linked between earth bars, earthing of all equipment and 70mm cables to all DB's | 1 | 0 | 0
7.2 | 1 x earth bar in each UPS room including 2 x 70mm earth cables to each earth bar fed from main building earth, 2 x 70mm earth linked between earth bars, earthing of all equipment and to all DB's | 1 | 0 | 0
7.21 | A and B UPS feeds to the monitoring systems in all 3 rooms | 1 | 0 | 0
7.22 | Rack mount 16A STS units | 6 | 0 | 0
7.23 | All routing in UPS rooms | 1 | 0 | 0
7.24 | Supply and install ATS units for DC cooling units | 2 | 0 | 0
7.25 | All routing in server room for light circuits, fire panel feeds, cooling unit feeds, fresh air unit feeds, etc. | 1 | 0 | 0
7.26 | Under floor routing for all electrical circuits A and B | 1 | 0 | 0
7.27 | Overhead routing for all data cables in server room | 1 | 0 | 0
7.28 | Supply and install ATS units for cooling units in UPS rooms | 4 | 0 | 0
8 | ELECTRICAL RETICULATION - LV Room
8.1 | UPS rectifier and bypass inputs including SWA electrical cable, ICEW cable, routing, lugs, glands, shrouds and terminations. Fed from generator sync changeover panel | 1 | 0 | 0
8.2 | UPS outputs including SWA electrical cable, ICEW cable, routing, lugs, glands, shrouds and terminations to feed existing UPS DB outside existing server room | 1 | 0 | 0
8.3 | LED lighting in room | 1 | 0 | 0
8.4 | Emergency lighting in room | 1 | 0 | 0
8.5 | Feeds to the cooling units in room fed from existing building DB | 2 | 0 | 0
8.6 | Feed to the fire system fed from existing building UPS DB | 1 | 0 | 0
8.7 | Feed to the monitoring system fed existing building UPS DB | 1 | 0 | 0
8.8 | General white plug circuits | 2 | 0 | 0
9 | GENERAL
9.1 | Sundries @ max 5% of Bill 3 value | 1 | 0 | 0
9.2 | Labour | 1 | 0 | 0
9.3 | PROVISIONAL SUM for Electrical Refurb in building floors for lighting, Sockets, isolators, earthing, DB clean-up | 1 | 0 | 0
9.4 | Any additional equipment necessary to complete the installation, but not allowed elsewhere in the bill of quantities. | 1 | 0 | 0
| Total Including Vat |  |  | 0

## 4. HVAC
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Unit | Qty | Rate | Total incl. VAT
4. HVAC
1 | SERVER ROOM CRAC UNITS
1.1 | Decommission and phased Removal of 2 x Existing Montair Down draft units from existing server room complete with control systems, wiring, electrics | No | 2 | 0 | 0
1.2 | Checking and servicing of x Existing Montair Down draft units. | No | 2 | 0 | 0
1.3 | Relocate and phased installation of existing downblow units in new server room ( exact position to be determined) complete with control systems, wiring, water connection for humidifier | No | 2 | 0 | 0
1.4 | Supply and installation of CRAC unit adjustable floor support stand/frames complete to accommodate 600mm floor void | No | 2 | 0 | 0
1.5 | Supply and installation of CRAC 90° galvanised duct bend outlet within floor void to suite. | No | 2 | 0 | 0
1.6 | Supply and installation of interconnecting refrigerant piping complete with piping insulation as described with bends, elbows, supports, connections ( 20 meters per unit) | m | 40 | 0 | 0
1.7 | Supply and installation of galvanised refrigerant piping trunking to exposed piping to match existing trunking installation on site. | Sum | 1 | 0 | 0
1.8 | Supply and installation of sleeves in wall penetrations complete with sealing thereof for room integrity | No | 2 | 0 | 0
1.9 | Upgrading of unit controls ( if required) to accommodate Monitoring system installed by others, as well as facilitating the interfacing of monitoring system. | Sum | 1 | 0 | 0
1.10 | All electrical works relating to the relocation process. | Sum | 1 | 0 | 0
1.11 | Supply and installation of floor mounted supply air grilles ( 600 x 600 to match existing grilles on site) | No | 8 | 0 | 0
1.12 | Supply and installation of 28mm condensate piping (copper) for each unit to nearest drain point provided by others complete with brackets, bend etc. (15 m per unit) | m | 30 | 0 | 0
1.13 | Supply and installation of status indicator/monitoring panel external to server room as described. (Fan Control Panel complete with forward-reverse controls with indication lights to indicate fan in forward or reverse, monitoring contacts for damper position and fan forward/reverse status, buzzer and warning light to indicate fan is in reverse. remote control status panel. Control panel to be mounted on external wall of Server Room | Sum | 1 | 0 | 0
1.14 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
2 | SERVER ROOM FRESH AIR/PURGE SYSTEM
Supply and installation of Fresh air/purge system complete with fan, indicator panel, VSD drive if required, ducting, louvres, controls, dampers complete and commissioned.
2.1 | Supply only of reversible fan system ( 250l/s, 350kPa estimated static) complete and commissioned | No | 1 | 0 | 0
2.2 | Supply and installation of 600 x 400 weather louvre located in UPS room external wall | No | 1 | 0 | 0
2.3 | Filter plenum to suite with accessible hingable access panel complete with filter systems as described | No | 1 | 0 | 0
2.4 | Transfer duct piece from filter plenum to 400 x 300 fresh air duct | No | 1 | 0 | 0
2.5 | 400 x 300 uninsulated straight duct through UPS room and penetrating into server room ceiling void. | m | 9 | 0 | 0
2.6 | 400 x 300 uninsulated duct bends to suite | No | 4 | 0 | 0
2.7 | Install 600 x 600 in-ceiling outlet grille natural anodised aluminium in server room ceiling complete with balancing damper | No | 1 | 0 | 0
2.8 | 400 x 300 fire damper installed in wall between UPS room and server room complete with actuator and control panel (120 min rated) | No | 1 | 0 | 0
2.9 | 600 x 400 fire damper installed in UPS room external wall complete with actuator and controls compatible with monitoring system by others (120 min rated) | No | 1 | 0 | 0
2.10 | All wiring and interfacing works relating to the purge, fresh air systems. | Sum | 1 | 0 | 0
2.11 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
3 | UPS ROOMS A & B (New Split units)
Supply and install Commercial/Industrial mid wall split, inverter complete including: Auto restart, Refrigerant, outdoor condenser, condensate drainage, support complete and commissioned
3.1 | Supply only of 24000 BTU total cooling industrial type midwall split unit | No | 4 | 0 | 0
3.2 | Supply of galvanised condenser support brackets to suite | No | 4 | 0 | 0
3.3 | Supply and installation of interconnecting refrigerant piping complete with piping insulation as described with bends, elbows, supports, connections ( 15 meters per unit x 4 units) | m | 60 | 0 | 0
3.4 | Supply and installation of galvanised refrigerant piping trunking to exposed piping to match existing trunking installation on site. | Sum | 1 | 0 | 0
3.5 | Supply and installation of sleeves in wall penetrations complete with sealing thereof for room integrity | No | 4 | 0 | 0
3.6 | Upgrading of unit controls ( if required) to accommodate Monitoring system installed by others, as well as facilitating the interfacing of monitoring system. | No | 4 | 0 | 0
3.7 | All electrical works relating to the relocation process. | Sum | 1 | 0 | 0
3.8 | Supply and installation individual status indicator/monitoring panel external to UPS room as described. (Control panel to incorporate fresh air system monitoring) | Sum | 2 | 0 | 0
3.9 | Supply and installation of 28mm condensate piping (copper) for each unit to nearest drain point provided by others complete with brackets, bend etc. (10 m per unit) | m | 40 | 0 | 0
3.10 | Commissioning of units | No | 4 | 0 | 0
3.11 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
4 | UPS ROOMS FRESH AIR
Supply and installation of Fresh air system complete with fan, indicator panel, VSD drive if required, ducting, louvres, controls, dampers complete and commissioned.
4.1 | Supply only of fresh air fan system ( 200l/s, 250kPa estimated static) complete and commissioned | No | 2 | 0 | 0
4.2 | Supply and installation of 500 x 400 weather louvre located in UPS room external wall | No | 2 | 0 | 0
4.3 | Filter plenum to suite with accessible hingable access panel complete with filter systems as described | No | 2 | 0 | 0
4.4 | Transfer duct piece from filter plenum to 400 x 300 fresh air duct | No | 2 | 0 | 0
4.5 | 400 x 300 uninsulated straight duct in UPS room | m | 10 | 0 | 0
4.6 | 400 x 300 uninsulated duct bends to suite | No | 4 | 0 | 0
4.7 | Install 400 x 400 outlet grille natural anodised aluminium in room complete with balancing damper | No | 2 | 0 | 0
4.8 | 500 x 400 fire damper installed in UPS room external wall complete with actuator and controls compatible with monitoring system by others (120 min rated) | No | 2 | 0 | 0
4.9 | All wiring and interfacing works relating to the fresh air systems. | Sum | 1 | 0 | 0
4.10 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
5 | LV ROOM (Existing split units )
remove, relocate and reinstall existing UPS room split and reinstall in LV room including: Refrigerant, outdoor condenser, condensate drainage, support complete and commissioned
5.1 | Decommission and Remove 2 x Existing underceiling split units in existing 1st floor UPS room complete with control systems, wiring, electrics | No | 2 | 0 | 0
5.2 | Checking and servicing of Existing units. | No | 2 | 0 | 0
5.3 | Relocate and install existing underceiling units in LV room ( exact position to be determined) complete with control systems, wiring, etc. | No | 2 | 0 | 0
5.4 | Supply of galvanised condenser support brackets to suite | No | 2 | 0 | 0
5.5 | Supply and installation of interconnecting refrigerant piping complete with piping insulation as described with bends, elbows, supports, connections ( 15 meters per unit x 2 units) | m | 30 | 0 | 0
5.6 | Supply and installation of galvanised refrigerant piping trunking to exposed piping to match existing trunking installation on site. | Sum | 1 | 0 | 0
5.7 | Supply and installation of sleeves in wall penetrations complete with sealing thereof for room integrity | No | 2 | 0 | 0
5.8 | Upgrading of unit controls to accommodate Monitoring system installed by others, as well as facilitating the interfacing of monitoring system. | No | 2 | 0 | 0
5.9 | All electrical works relating to the relocation process. | Sum | 1 | 0 | 0
5.10 | Supply and installation individual status indicator/monitoring panel external to LV room as described. (Control panel to incorporate fresh air system monitoring) | Sum | 1 | 0 | 0
5.11 | Supply and installation of 28mm condensate piping (copper) for each unit to nearest drain point provided by others complete with brackets, bend etc. (10 m per unit) | m | 20 | 0 | 0
5.12 | Commissioning of units | No | 2 | 0 | 0
5.13 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
6 | LV ROOM FRESH AIR
Supply and installation of Fresh air system complete with fan, indicator panel, VSD drive if required, ducting, louvres, controls, dampers complete and commissioned.
6.1 | Supply only of fresh air fan system ( 400l/s, 250kPa estimated static) complete and commissioned | No | 1 | 0 | 0
6.2 | Supply and installation of 600 x 400 weather louvre located in UPS room external wall | No | 1 | 0 | 0
6.3 | Filter plenum to suite with accessible hingable access panel complete with filter systems as described | No | 1 | 0 | 0
6.4 | Transfer duct piece from filter plenum to 400 x 300 fresh air duct | No | 1 | 0 | 0
6.5 | 400 x 300 uninsulated straight duct in LV room | m | 10 | 0 | 0
6.6 | 400 x 300 uninsulated duct bends to suite | No | 4 | 0 | 0
6.7 | Install 400 x 400 outlet grille natural anodised aluminium in room complete with balancing damper | No | 1 | 0 | 0
6.8 | 600 x 400 fire damper installed in LV room external wall complete with actuator and controls compatible with monitoring system by others (120 min rated) | No | 2 | 0 | 0
6.9 | All wiring and interfacing works relating to the fresh air systems. | Sum | 1 | 0 | 0
6.10 | Other not mentioned above : ( include description) | Sum | 1 | 0 | 0
7 | GENERAL
7.1 | Removal and relocation of existing York condenser units to new position to make way for UPS room construction complete with piping, electrics and recommissioning |  |  | 0 | 0
7.2 | Sundries for all | Sum | 1 | 0 | 0
7.3 | Any additional equipment necessary to complete the installation, but not allowed elsewhere in the bill of quantities. ( describe) | Sum | 1 | 0 | 0
| Total Including Vat |  |  |  | 0

## 5. GENERAL
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Qty | Rate | Total incl. VAT
5. GENERAL ITEMS
1 | GENERAL
1.1 | P&G's | 1 | 0 | 0
1.2 | Project Management and Site Supervision | 1 | 0 | 0
1.3 | Health and Safety | 1 | 0 | 0
1.4 | As-Built drawings | 3 | 0 | 0
1.5 | Maintenance and operations manuals | 3 | 0 | 0
1.6 | Training of operators | 1 | 0 | 0
1.7 | Workmanship Guarantee for 12 months over and above product guarantees | 1 | 0 | 0
1.8 | Labelling and Numbering of Racks, PDUs, Input power cables, etc. | 1 | 0 | 0
1.9 | Individual systems testing | 1 | 0 | 0
1.1 | Integrated systems testing | 1 | 0 | 0
1.11 | Load bank for UPS battery discharge runtime tests onsite | 1 | 0 | 0
1.12 | Heaters for server room cooling tests | 1 | 0 | 0
1.13 | Handover files | 1 | 0 | 0
| Total Including Vat |  |  | 0

## 6. 5yr Maintenance
SOUTH AFRICAN NURSING COUNCIL SERVER ROOM
Item | Description | Qty | Rate | Total incl. VAT
6. 5yr Maintenance
1 | GENERATOR
1.1 | Year 1 quarterly maintenance of the 1 x 400kVA and 1 x 200kVA generator including 3 x minor services and 1 x Major service | 1 | 0 | 0
1.2 | Year 2 quarterly maintenance of the 1 x 400kVA and 1 x 200kVA generator including 3 x minor services and 1 x Major service | 1 | 0 | 0
1.3 | Year 3 quarterly maintenance of the 1 x 400kVA and 1 x 200kVA generator including 3 x minor services and 1 x Major service | 1 | 0 | 0
1.4 | Year 4 quarterly maintenance of the 1 x 400kVA and 1 x 200kVA generator including 3 x minor services and 1 x Major service | 1 | 0 | 0
1.5 | Year 5 quarterly maintenance of the 1 x 400kVA and 1 x 200kVA generator including 3 x minor services and 1 x Major service | 1 | 0 | 0
2 | UPS
2.1 | Year 1 quarterly maintenance of the 2 x 60kVA UPS's and the 1 x Modular UPS | 1 | 0 | 0
2.2 | Year 2 quarterly maintenance of the 2 x 60kVA UPS's and the 1 x Modular UPS | 1 | 0 | 0
2.3 | Year 3 quarterly maintenance of the 2 x 60kVA UPS's and the 1 x Modular UPS | 1 | 0 | 0
2.4 | Year 4 quarterly maintenance of the 2 x 60kVA UPS's and the 1 x Modular UPS | 1 | 0 | 0
2.5 | Year 5 quarterly maintenance of the 2 x 60kVA UPS's and the 1 x Modular UPS | 1 | 0 | 0
3 | Air-Conditioning (To be obtained from existing contractor)
3.1 | Year 1 monthly maintenance of the cooling in the server room, cooling units in both UPS room, cooling units in the LV room and the fresh air system in the server room | 1 | 0 | 0
3.1 | Year 2 monthly maintenance of the cooling in the server room, cooling units in both UPS room, cooling units in the LV room and the fresh air system in the server room | 1 | 0 | 0
3.3 | Year 3 monthly maintenance of the cooling in the server room, cooling units in both UPS room, cooling units in the LV room and the fresh air system in the server room | 1 | 0 | 0
3.4 | Year 4 monthly maintenance of the cooling in the server room, cooling units in both UPS room, cooling units in the LV room and the fresh air system in the server room | 1 | 0 | 0
3.5 | Year 5 monthly maintenance of the cooling in the server room, cooling units in both UPS room, cooling units in the LV room and the fresh air system in the server room | 1 | 0 | 0
4 | Fire Systems
4.1 | Year 1 quarterly maintenance of the fire systems in the server room, UPS rooms and the LV room | 1 | 0 | 0
4.2 | Year 2 quarterly maintenance of the fire systems in the server room, UPS rooms and the LV room | 1 | 0 | 0
4.3 | Year 3 quarterly maintenance of the fire systems in the server room, UPS rooms and the LV room | 1 | 0 | 0
4.4 | Year 4 quarterly maintenance of the fire systems in the server room, UPS rooms and the LV room | 1 | 0 | 0
4.5 | Year 5 quarterly maintenance of the fire systems in the server room, UPS rooms and the LV room | 1 | 0 | 0
5 | Monitoring System
5.1 | Year 1 quarterly maintenance of the monitoring systems in the server room, UPS rooms, generators and the LV room | 1 | 0 | 0
5.2 | Year 2 quarterly maintenance of the monitoring systems in the server room, UPS rooms, generators and the LV room | 1 | 0 | 0
5.3 | Year 3 quarterly maintenance of the monitoring systems in the server room, UPS rooms, generators and the LV room | 1 | 0 | 0
5.4 | Year 4 quarterly maintenance of the monitoring systems in the server room, UPS rooms, generators and the LV room | 1 | 0 | 0
5.5 | Year 5 quarterly maintenance of the monitoring systems in the server room, UPS rooms, generators and the LV room | 1 | 0 | 0
5.6 | Year 1 renewal on all the TM4 units, unlimited SMS's, care report and weekly testing | 1 | 0 | 0
5.7 | Year 2 renewal on all the TM4 units, unlimited SMS's, care report and weekly testing | 1 | 0 | 0
5.8 | Year 3 renewal on all the TM4 units, unlimited SMS's, care report and weekly testing | 1 | 0 | 0
5.9 | Year 4 renewal on all the TM4 units, unlimited SMS's, care report and weekly testing | 1 | 0 | 0
5.1 | Year 5 renewal on all the TM4 units, unlimited SMS's, care report and weekly testing | 1 | 0 | 0
6 | Deep Impact Clean
6.1 | Year 1 deep impact cleaning of the server room and UPS rooms done twice a year including under floor, above floor and equipment surfaces | 1 | 0 | 0
6.2 | Year 2 deep impact cleaning of the server room and UPS rooms done twice a year including under floor, above floor and equipment surfaces | 1 | 0 | 0
6.3 | Year 3 deep impact cleaning of the server room and UPS rooms done twice a year including under floor, above floor and equipment surfaces | 1 | 0 | 0
6.4 | Year 4 deep impact cleaning of the server room and UPS rooms done twice a year including under floor, above floor and equipment surfaces | 1 | 0 | 0
6.5 | Year 5 deep impact cleaning of the server room and UPS rooms done twice a year including under floor, above floor and equipment surfaces | 1 | 0 | 0
| Total Including Vat |  |  | 0